## BOQ-1-Waste Water
WASTEWATER COLLECTION NETWORK SYSTEM - PIC_SEZ , ROC_R2
S.No. | Description of Item | Unit | Qtty | Supply |  | Erection |  | Total
|  |  |  | Rate | Amount | Rate | Amount | Rate | Amount
1 | Excavation in trenches, manholes, pipe lines, foundations, column footings, walls etc. in earth’s soils of all types, gravel, sand, soft & hard murum, and boulders up to 0.03 cum. size including removing the excavated material upto a distance of 50 M beyond the edge of excavation including the initial lift of 1.5 M, stacking or spreading as directed, bailing of sub-soil water if any preparing base for foundation, dressing etc., as directed by Engineer-In-charge, including all labour and materials complete as per the instructions of Engineer-in-Charge.
a | For depth up to 1.5 m | Cum | 31220 |  | 0 |  | 0 | 0 | 0
b | for depth 1.5 to 2.5 m | Cum | 3710 |  | 0 |  | 0 | 0 | 0
c | For depth between 2.5m to 3.5m | Cum | 20 |  | 0 |  | 0 | 0 | 0
2 | Supply, delivery at work site coarse sand and filling the pipeline trenches for bedding of pipes including watering, ramming as per the instructions of Engineer-in-Charge including cost and conveyance of material, labour charges and all other incidental and operational charges complete. |  | 0
a | below pipeline trenches /Manholes | Cum | 1739 |  | 0 |  | 0 | 0 | 0
3 | Laying of CC(1:3:6) using coarse and fine aggregates conforming to standard codes and guidelines including cost and conveyance of all materials, labour charges, machine mixing, vibration, centering, laying in position, curing etc complete for Base Course as per the instructions of Engineer-in-Charge below Pipeline Trenches or manholes
a | below pipeline trenches /Manholes | Cum | 11 |  | 0 |  | 0 | 0 | 0
4 | Laying of CC(1:2:4) using 20mm nominal size machine crushed stone aggregate, machine mixing including cost and conveyance of all materials and labour charges, tamping, benching, dressing to true alignment and curing including all operational and incidental charges etc., complete different works as per the instructions of Engineer-in-Charge
a | for Benching of Manholes /Pipeline Crossings/ Bedding in walls for every 1 m height of wall, PPC Anchor blocks -1 nos between two manholes etc. | Cum | 330 |  | 0 |  | 0 | 0 | 0
5 | Lowering, laying, cutting and jointing (electro-fusion method) of HDPE PE80 Grade 8.0 kg/sqcm conforming to European / ISO / International Standards to carry and convey wastewater/ sewage/ industrial effluent and laying in trenches to true alignment following design gradient over the prepared base including all material, transporation, laying, jointing, labour charges, testing charges complete as per the instructions of Engineer-in-Charge
a | 160mm OD | Rmt | 570 | Free Issue |  |  | 0 | 0 | 0
b | 180mm OD | Rmt | 470 | Free Issue |  |  | 0 | 0 | 0
c | 225 mm OD | Rmt | 12180 | Free Issue |  |  | 0 | 0 | 0
d | 250mm OD | Rmt | 1560 | Free Issue |  |  | 0 | 0 | 0
e | 280mm OD | Rmt | 970 | Free Issue |  |  | 0 | 0 | 0
f | 355mm OD | Rmt | 850 | Free Issue |  |  | 0 | 0 | 0
g | 450mm OD | Rmt | 350 | Free Issue |  |  | 0 | 0 | 0
6 | Masonry work for Construction of sewer square manholes as per details of type design in Brick/RCC Block Masonry (Solid Block) (1:4) 200mm thick with standard cement concrete blocks to required height over the prepared PCC bed leaving provision for embedding inlet and outlet pipes, FRP encapsulated steps etc., with neat finishing, dressing, etc., including scaffolding, centering works and cost and conveyance of all other incidential and operational charges etc., complete.
a | for Manholes upto 2.5m height | Cum | 540 |  | 0 |  | 0 | 0 | 0
7 | Internal Plastering using CM(1:3) for manhole walls preferably with Sulphate Resistance Cement with neat finishing, curing etc., including the cost and conveyance of all other incidental and operational charges etc., complete
a | for Manholes | Sqm | 3396 |  | 0 |  | 0 | 0 | 0
8 | RCC M25 using 20mm nominal size machine crushed stone aggregate, machine mixing including cost and conveyance of all materials and labour charges, centring, scaffolding but excluding the cost of reinforcement including all operational and incidental charges etc., complete for Manhole Cover Slab as per the instructions of Engineer-in-Charge
a | Manhole Cover Slab | Cum | 98 |  | 0 |  | 0 | 0 | 0
9 | Supply of steel reinforcement Fe415 or above grade including fabrication, placing in position, binding, cutting, jointing, etc., including cost and conveyance of material, labour charges, cost of binding wire, cost of epoxy coat etc., as per the instruction of Engineer-in-Charge
a | Steel | Kg | 9800 |  | 0 |  | 0 | 0 | 0
10 | Supply and fixing of Fiber encapsulated steps medium weight each in manholes including cost and conveyance of all materials to site, labour charges, all incidental and operational charges etc., complete inside the manholes
a | Encapsulated steps for Manholes | Nos. | 1710 |  | 0 |  | 0 | 0 | 0
11 | Supplying and fixing heavy duty fibre reinforced concrete man hole frame (SFRC) and cover of clear sizes of 600mm x 600mm complying to International Standards including cost and conveyance of materials, labour charges, all other incidental and operational charges etc., complete
a | Manhole Covers | Nos. | 382 |  | 0 |  | 0 | 0 | 0
12 | Refilling the pipeline and manhole trenches with excavated useful soils other than sand complying with standard specifications including watering and tamping in layers of 225mm thick including all other operational and incidental charges etc., complete.
a | in pipeline trenches /Manhole Trenches | Cum | 27440 |  | 0 |  | 0 | 0 | 0
13 | Carting of surplus excavated soil/rock from pipeline and manhole trenches to a suitable distance including loading, unloading charges cost and conveyance and labour charges, all lifts and other incidental and operational charges etc., complete as per the instructions of Engineer-in-Charge
a | surplus pipeline earth /Manhole earth | Cum | 3820 |  | 0 |  | 0 | 0 | 0
14 | Supply and fixing of HDPE PE80 PN6 Grade End Caps of specified size including jointing by suitable methods including the cost of material, labour, jointing etc., complete as per the instructions of Engineer-in-Charge
a | HDPE End Caps - 160mm OD | Nos | 57 |  | 0 |  | 0 | 0 | 0
b | HDPE End Caps - 180mm OD | Nos | 47 |  | 0 |  | 0 | 0 | 0
c | HDPE End Caps - 225mm OD | Nos | 26 |  | 0 |  | 0 | 0 | 0
| Total Amount |  |  |  | 0 |  | 0 |  | 0

## BOQ-2- Dist. System
PIC- PNR -ROC - BOQ- WATER SUPPLY DISTRIBUTION NETWORK
Sl. No. | Description of work | Unit | Qtty | Supply |  | Erection |  | Total
|  |  |  | Rate | Amount | Rate | Amount | Rate | Amount
1 | Excavation in trenches, manholes, pipe lines, foundations, column footings, walls etc. in earth’s soils of all types, gravel, sand, soft & hard murum, and boulders up to 0.03 cum. size including removing the excavated material upto a distance of 50 M beyond the edge of excavation including the initial lift of 1.5 M, stacking or spreading as directed, bailing of sub-soil water if any preparing base for foundation, dressing etc., as directed by Engineer-In-charge, including all labour and materials complete as per the instructions of Engineer-in-Charge.
a | For depth up to 1.5m | Cum | 20754 |  | 0 |  | 0 | 0 | 0
2 | Supply, delivery at work site coarse sand and filling the pipeline trenches for bedding of pipes including watering, ramming as per the instructions of Engineer-in-Charge including cost and conveyance of material, labour charges and all other incidental and operational charges complete.
a | below pipeline trenches | Cum | 671 |  | 0 |  | 0 | 0 | 0
3 | Lowering, laying, cutting and jointing (electro-fusion method) of HDPE pipes (Grade PE-100 PN- 10.0 Kg/sqcm) conforming to ISO 4427 / EN 805: 2000 /ISO 12176: 2003 or equivalent standards to carry and convey potable water/borewell water and laying in trenches to true alignment following design gradient over the prepared base including all material, transportation, laying, jointing, labour charges, testing charges complete but excluding the cost of Specials as per the instructions of Engineer-in-Charge
a | 25mm OD | Rmt | 320 | Free Issue |  |  | 0 | 0 | 0
b | 32mm OD | Rmt | 310 | Free Issue |  |  | 0 | 0 | 0
c | 50mm OD | Rmt | 290 | Free Issue |  |  | 0 | 0 | 0
d | 63mm OD | Rmt | 240 | Free Issue |  |  | 0 | 0 | 0
e | 90 mm OD | Rmt | 30 | Free Issue |  |  | 0 | 0 | 0
f | 110mm OD | Rmt | 110 | Free Issue |  |  | 0 | 0 | 0
g | 180mm OD | Rmt | 11836 | Free Issue |  |  | 0 | 0 | 0
h | 250mm OD | Rmt | 4574 | Free Issue |  |  | 0 | 0 | 0
i | 400mm OD | Rmt | 268 | Free Issue |  |  | 0 | 0 | 0
4 | Manufacture, Supply and delivery of Ductile Iron D/F Gate/Sluice Valves of PN 10 conforming to ISO 5996, ISO 7259, EN 1171 and EN 1074-1-2 or Equivalent with hand wheel of Resilient seal type, with screwless bonnet connection, with easy assembly and dismantling of functioning parts, fully covered with EPDM elastomer and the valves should be of vacuum tight and 100% leak proof with face to face dimensions as per ISO 5752 – EN 558, Body and the cover must be fully protected with 250 micron\min, fusion bond high temperature Epoxy coating, relevant standards marked on valves complete as per standard specifications
a | 150mm dia | Nos | 21 |  | 0 | NA |  | 0 | 0
b | 200mm dia | Nos | 2 |  | 0 | NA |  | 0 | 0
d | 300mm dia | Nos | 1 |  | 0 | NA |  | 0 | 0
5 | Lowering, keeping in position and fixing Ductile Iron Sluice valves including cost of bolts, nuts, rubber insertion, and tail pieces etc., complete as per standard international working procedures
a | 150mm dia | Nos | 21 |  | 0 |  | 0 | 0 | 0
b | 200mm dia | Nos | 2 |  | 0 |  | 0 | 0 | 0
c | 300mm dia | Nos | 1 |  | 0 |  | 0 | 0 | 0
6 | Manufacture, Supply and delivery of Ductile Iron D/F Scour Valves of PN 10 conforming to ISO 5996, ISO 7259, EN 1171 and EN 1074-1-2 or Equivalent with hand wheel of Resilient seal type, with screwless bonnet connection, with easy assembly and dismantling of functioning parts, fully covered with EPDM elastomer and the valves should be of vacuum tight and 100% leak proof with face to face dimensions as per ISO 5752 – EN 558, Body and the cover must be fully protected with 250 micron\min, fusion bond high temperature Epoxy coating, relevant standards marked on valves complete as per standard specifications
a | 50mm dia | Nos | 10 |  | 0 | NA |  | 0 | 0
7 | Lowering, keeping in position and fixing Ductile Iron Scour valves including cost of bolts, nuts, rubber insertion, and tail pieces etc., complete as per standard international working procedures
a | 50mm dia | Nos | 10 |  | 0 |  | 0 | 0 | 0
8 | Laying of CC(1:3:6) using coarse and fine aggregates conforming to standard codes and guidelines including cost and conveyance of all materials, labour charges, machine mixing, vibration, centring, laying in position, curing etc complete for Base Course for Valve Chambers as per the instructions of Engineer-in-Charge
a | for Sluice and Scour Valve Chambers | Cum | 11 |  | 0 |  | 0 | 0 | 0
9 | Masonry work for Construction of Valve Chambers as per details of type design in Brick Masonry/ 200mm thick CC Block (1:4) with standard cement concrete blocks to required height over the prepared PCC bed leaving provision for embedding inlet and outlet pipes, with neat finishing, dressing, etc., including scaffolding, centring works and cost and conveyance of all other incidentals and operational charges etc., complete.
a | for Sluice and Scour Valve Chambers | Cum | 47 |  | 0 |  | 0 | 0 | 0
10 | RCC M25 using 20mm nominal size machine crushed stone aggregate, machine mixing including cost and conveyance of all materials and labour charges, centring, scaffolding but excluding the cost of reinforcement including all operational and incidental charges etc., complete for Valve Chamber Cover Slab as per the instructions of Engineer-in-Charge
a | for Sluice and Scour Valve Chambers | Cum | 7 |  | 0 |  | 0 | 0 | 0
11 | Supply of steel reinforcement Fe415 or above grade including fabrication, placing in position, binding, cutting, jointing, etc., including cost and conveyance of material, labour charges, cost of binding wire, cost of epoxy coat etc., as per the instruction of Engineer-in-Charge
a | for Sluice and Scour Valve Chambers | Kg | 569 |  | 0 |  | 0 | 0 | 0
12 | Supplying and fixing heavy duty fibre reinforced concrete man hole frame and cover of clear sizes of 300mm diameter complying to International Standards including cost and conveyance of materials, labour charges, all other incidental and operational charges etc., complete
a | for Sluice and Scour Valve Chambers | Nos | 24 |  | 0 |  | 0 | 0 | 0
13 | Manufacture, Supply, delivery, lowering and laying of R.C.C. Plain ended Pipes NP3 - Class Pipes through to the alignment confirming to European/French/ other International Standards, including the cost of specials, collars etc., transportation cost etc., as per the instruction of Engineer-in-Charge
a | 100mm dia for encasing HSC HDPE pipelines below road surface | Rmt | 630 |  | 0 |  | 0 | 0 | 0
b | 150mm dia for encasing HSC HDPE pipelines below road surface | Rmt | 530 |  | 0 |  | 0 | 0 | 0
c | 200mm dia for encasing HSC HDPE pipelines below road surface | Rmt | 140 |  | 0 |  | 0 | 0 | 0
14 | Laying of CC(1:2:4) using 20mm nominal size machine crushed stone aggregate, machine mixing including cost and conveyance of all materials and labour charges, tamping, to true alignment and curing including all operational and incidental charges etc., complete different works as per the instructions of Engineer-in-Charge
a | For encasing pipes at road crossings | Cum | 30.615 |  | 0 |  | 0 | 0 | 0
15 | Provision and fixing of HDPE PN 10 PE100 electro fusion tapping saddles for providing property service connections including ferrule, adopters, bends, labour charges, jointing etc., All Materials shall be EN, ISO or equivalent standard and shall be supplied from approved manufacturers. complete
a | 180mm x 25mm | Nos | 23 |  | 0 |  | 0 | 0 | 0
b | 180mm x 32mm | Nos | 25 |  | 0 |  | 0 | 0 | 0
c | 180mm x 50mm | Nos | 19 |  | 0 |  | 0 | 0 | 0
d | 180mm x 63mm | Nos | 16 |  | 0 |  | 0 | 0 | 0
e | 180mm x 90mm | Nos | 2 |  | 0 |  | 0 | 0 | 0
f | 180mm x 110mm | Nos | 10 |  | 0 |  | 0 | 0 | 0
g | 250mm x 25mm | Nos | 9 |  | 0 |  | 0 | 0 | 0
h | 250mm x 32mm | Nos | 6 |  | 0 |  | 0 | 0 | 0
i | 250mm x 50mm | Nos | 8 |  | 0 |  | 0 | 0 | 0
j | 250mm x 63mm | Nos | 7 |  | 0 |  | 0 | 0 | 0
k | 250mm x 90mm | Nos | 1 |  | 0 |  | 0 | 0 | 0
l | 250mm x 110mm | Nos | 1 |  | 0 |  | 0 | 0 | 0
m | 400mm x 50mm | Nos | 2 |  | 0 |  | 0 | 0 | 0
n | 400mm x 63mm | Nos | 1 |  | 0 |  | 0 | 0 | 0
16 | Provision and lowering of HDPE specials with electro-fusion joints in Distribution: Bends, reducers, enlargers and Tee joints of PE-100 grade with pressure rating of PN-10. End connections: Electro fusion joints as per BS: EN 1555-3, EN 12201-3, ISO: 8085-3
i | Tee Joints
a | 180 x 180 x 180 mm | Nos | 57 |  | 0 |  | 0 | 0 | 0
b | 250 x 250 x 250 mm | Nos | 11 |  | 0 |  | 0 | 0 | 0
c | 400 x 400 x 400 mm | Nos | 4 |  | 0 |  | 0 | 0 | 0
ii | Bends - 450
a | 25 mm | Nos | 0 |  | 0 |  | 0 | 0 | 0
b | 32 mm | Nos | 0 |  | 0 |  | 0 | 0 | 0
c | 50 mm | Nos | 0 |  | 0 |  | 0 | 0 | 0
d | 63 mm | Nos | 0 |  | 0 |  | 0 | 0 | 0
e | 90 mm | Nos | 0 |  | 0 |  | 0 | 0 | 0
f | 110 mm | Nos | 0 |  | 0 |  | 0 | 0 | 0
g | 180 mm | Nos | 40 |  | 0 |  | 0 | 0 | 0
h | 250 mm | Nos | 15 |  | 0 |  | 0 | 0 | 0
i | 400 mm | Nos | 16 |  | 0 |  | 0 | 0 | 0
iii | Bends - 900
a | 25 mm | Nos | 96 |  | 0 |  | 0 | 0 | 0
b | 32 mm | Nos | 93 |  | 0 |  | 0 | 0 | 0
c | 50 mm | Nos | 87 |  | 0 |  | 0 | 0 | 0
d | 63 mm | Nos | 72 |  | 0 |  | 0 | 0 | 0
e | 90 mm | Nos | 9 |  | 0 |  | 0 | 0 | 0
f | 110 mm | Nos | 33 |  | 0 |  | 0 | 0 | 0
g | 180 mm | Nos | 120 |  | 0 |  | 0 | 0 | 0
h | 250 mm | Nos | 55 |  | 0 |  | 0 | 0 | 0
i | 400 mm | Nos | 53 |  | 0 |  | 0 | 0 | 0
vi | Reducers
a | 400 x 250 mm | Nos | 6 |  | 0 |  | 0 | 0 | 0
b | 400 x 180 mm | Nos | 4 |  | 0 |  | 0 | 0 | 0
c | 250 x 180 mm | Nos | 7 |  | 0 |  | 0 | 0 | 0
d | 180 x 150 mm | Nos | 8 |  | 0 |  | 0 | 0 | 0
vii | HDPE Flange Adopters of 400-600 mm Long
a | 150mm dia | Nos | 42 |  | 0 |  | 0 | 0 | 0
b | 200mm dia | Nos | 4 |  | 0 |  | 0 | 0 | 0
d | 300mm dia | Nos | 2 |  | 0 |  | 0 | 0 | 0
viii | HDPE with D/F Flanges 200-400 mm long Dismantling piece
a | 25 mm | Nos | 32 |  | 0 |  | 0 | 0 | 0
b | 32 mm | Nos | 31 |  | 0 |  | 0 | 0 | 0
c | 50 mm | Nos | 29 |  | 0 |  | 0 | 0 | 0
d | 63 mm | Nos | 24 |  | 0 |  | 0 | 0 | 0
e | 90 mm | Nos | 3 |  | 0 |  | 0 | 0 | 0
f | 110 mm | Nos | 11 |  | 0 |  | 0 | 0 | 0
g | 180 mm | Nos | 24 |  | 0 |  | 0 | 0 | 0
h | 250 mm | Nos | 2 |  | 0 |  | 0 | 0 | 0
ix | HDPE Puddle piece
a | 180 mm Dia | Nos | 56 |  | 0 |  | 0 | 0 | 0
b | 225 mm Dia | Nos | 10 |  | 0 |  | 0 | 0 | 0
c | 280 mm Dia | Nos | 2 |  | 0 |  | 0 | 0 | 0
17 | Refilling the pipeline and manhole trenches with excavated useful soils other than sand complying with standard specifications including watering and tamping in layers of 225mm thick including all other operational and incidental charges etc., complete as per the instructions of Engineer-in-Charge
a | in pipeline trenches | Cum | 18430 |  | 0 |  | 0 | 0 | 0
18 | Carting of surplus excavated soil/rock from pipeline and manhole trenches to a suitable distance including loading, unloading charges cost and conveyance and labour charges, all lifts and other incidental and operational charges etc., complete as per the instructions of Engineer-in-Charge
a | Carting surplus earth | Cum | 1247 |  | 0 |  | 0 | 0 | 0
19 | Lowering, keeping in position and fixing Ductile Iron Automatic Air valves including cost of bolts, nuts, rubber insertion, tail pieces etc., complete as per standard international working procedures
a | 40mm dia | Nos | 2 |  | 0 |  | 0 | 0 | 0
20 | Supply, Delivery and Fixing of Cast Iron / Ductile Iron made Ball Valves (stainless steel ball) for the Property Service Connection conforming to International Standard specifications, including cost of material, labour etc., complete as per instructions of Engineer-in-Charge
a | 25 mm | Nos | 32 |  | 0 |  | 0 | 0 | 0
b | 32 mm | Nos | 31 |  | 0 |  | 0 | 0 | 0
c | 50 mm | Nos | 29 |  | 0 |  | 0 | 0 | 0
d | 63 mm | Nos | 24 |  | 0 |  | 0 | 0 | 0
e | 90 mm | Nos | 3 |  | 0 |  | 0 | 0 | 0
f | 110 mm | Nos | 11 |  | 0 |  | 0 | 0 | 0
21 | Supplying and laying of 100mm diameter 4.8mm thick MS Class ERW pipe with cement mortar internal lining including fittings, jointing, trenching and refilling etc., conforming to European or ISO standards complete as per the instruction of Engineer-in-Charge
a | MS pipe and fittings for EXTERNAL FIRE HYDRANT | Rmt | 108 |  | 0 |  | 0 | 0 | 0
22 | Supplying and fixing of (Hydrant) CI Sluice valves (with cap) as per relevant EN or ISO standards including the cost of stand post, duck foot bend, 100mm dia sluice valve, spacer and reducer with all jointing materials, gaskets, bolts, nuts, washers including labour charges complete for successful commission of hydrants
a | for External Fire Hydrant (valves and fittings) | Nos | 18 |  | 0 |  | 0 | 0 | 0
23 | RCC M30 using 20mm nominal size machine crushed stone aggregate, machine mixing including cost and conveyance of all materials and labour charges, centring, scaffolding but excluding the cost of reinforcement including all operational and incidental charges etc., complete for Anchor Block as per the instructions of Engineer-in-Charge | Cum | 100 |  | 0 |  | 0 | 0 | 0
24 | Supply of steel reinforcement Fe415 or above grade including fabrication, placing in position, binding, cutting, jointing, etc., including cost and conveyance of material, labour charges, cost of binding wire, cost of epoxy coat etc., as per the instruction of Engineer-in-Charge
a | for Anchor Block | Kg | 7900 |  | 0 |  | 0 | 0 | 0
| Grand Total |  |  |  | 0 |  | 0 |  | 0