## Updated BoQ
BILL OF QUANTITY - STREET LIGHT INSTALLATION, TESTING AND COMMISSIONING WORKS. PN SEZ - ROC
Sr. No. | Item Description | Unit | Qty. | Unit Rate (CFA) | Total Amount (CFA)
STREET LIGHT INSTALLATION WORKS INCLUDING TESTING & COMISSIONING
1 | Street Light Foundation Works, all as per attached Layout Drgs, Foundation Drgs, Foundation Designs :
Ref : Drg No # ARISE IIP/PICP/PN/TD/EL/SL-01/05
Ref : Drg No # EPC-SL-23-57270-10M-FDN-GAD-001
Ref : Foundation Design # EX000644-10M OP(1.5m SA 0.5m CA)_PLATEFORMES INDUSTRIELLES_R0-SK-FdnCal
Ref : Foundation Design # EX000644-10M OP(1.5m DA)_PLATEFORMES INDUSTRIELLES_R0-SK-FdnCal
Ref: EX000621-16M_HM(250W_12F)_PLATEFORMES INDUSTRIELLES_R0_SK
1.1 | Construct Street Lighting Foundation as per above technical details, c/w | No | 289 |  | 0
- PCC C15 grade 75mm thk
- RCC of M20 Class
- Re-Inforcement Steel as per drg.
- Anchor Bolts, duly aligned with Template
- 63mm Dia Flexible Conduit for Cable Entry & Exit
- Excavate & Back Fill, restore the site Back to normal.
1.2 | Construct Foundation 16m high mast flood light as per above technical details, c/w | No | 2 |  | 0
- PCC C15 grade 100mm thk
- RCC of M20 Class
- Re-Inforcement Steel as per drg.
- Anchor Bolts, duly aligned with Template
- 75mm Dia Flexible Conduit for Cable Entry & Exit
- Excavate & Back Fill, restore the site Back to normal.
2 | Installation of Street Light Poles - all as per attached Layout Drgs, SL Pole GA Drg :
Ref : Drg No # ARISE IIP/PICP/PN/TD/DEL/SL-01/05
Ref : Drg No # EPC-SL-23-57270-10M-GAD-001
Ref : Drg No # EPC-SL-23-57270-10M-GAD-002
2.1 | Installation of 10M - Single Arm Street Lgiht Pole with Decorative Bracket, c/w … | No | 214 |  | 0
- Assembling Street Light Pole
- Assembly of 170W / 200W Light Fitting together with 3C X 2.5sqmm Cu PVC Flexible Cable, duly terminated on both ends.
- Erect SL Pole all as per drg. on the foundations
2.2 | Installation of 10M - Double Arm Street Lgiht Pole with Decorative Bracket, c/w .No | No | 75 |  | 0
- Assembling Street Light Pole
- Assembly of 170W / 200W Light Fittings together with 3C X 2.5sqmm Cu PVC Flexible Cable, duly terminated on both ends.
- Erect SL Pole all as per drg. on the foundations.
2.3 | Installation of 16M - high mast pole complete with raising and lower system | No | 2 |  | 0
- Assembling high mast Pole
- Assembly of 12nr of 250w LED flood light fittings together with 3C X 2.5sqmm Cu PVC Flexible Cable, duly terminated on both ends.
- Erect high mast as per drg. on the foundations.
3 | Underground Cabling Works :
Ref : Drg No # ARISE IIP/PICP/PN/TD/EL/SL-01/05
Ref : Drg No # EPC-SL-23-57270-10M-GAD-001
Ref : Drg No # EPC-SL-23-57270-10M-GAD-002
Ref : Drg No # ARISE IIP/PICP/PN/TD/EL/SL-04
Ref : Drg No # ARISE IIP/PICP/PN/TD/EL/SL-05
Ref : Drg No # ARISE IIP/PICP/PN/TD/EL/SL-02
Excavate Cable Trenches of 300mm W X 750mm deep, Install the following cables of 1.1kV, Cu. Ar. XLPE Cables, direct in ground including excavation, sand cushioning, protective covering as per the drgs. c/w warning tape, bricks, and sand and back fill, restore the site back to normal.
3.1 | 5C x 35 Sq.mm from 25KVA SL Transformer LV side to SL Feeder Pillar # 1 | RM | 20 |  | 0
3.2 | Terminate the cble on both ends c/w Cable Glands, Lugs etc. | Set | 2 |  | 0
3.3 | 5C x 35 Sq.mm from 50KVA SL Transformer LV side to SL Feeder Pillar # 2 | RM | 20 |  | 0
3.4 | Terminate the cble on both ends c/w Cable Glands, Lugs etc. | Set | 2 |  | 0
3.5 | 5C x 35 Sq.mm from 25KVA SL Transformer LV side to SL Feeder Pillar # 3 | RM | 20 |  | 0
3.6 | Terminate the cble on both ends c/w Cable Glands, Lugs etc. | Set | 2 |  | 0
3.7 | 5C x 35 Sq.mm from 25KVA SL Transformer LV side to SL Feeder Pillar # 4 | RM | 20 |  | 0
3.8 | Terminate the cble on both ends c/w Cable Glands, Lugs etc. | Set | 2 |  | 0
3.9 | 5C x 35 Sq.mm from 25KVA SL Transformer LV side to SL Feeder Pillar # 5 | RM | 20 |  | 0
3.1 | Terminate the cble on both ends c/w Cable Glands, Lugs etc. | Set | 2 |  | 0
3.11 | 5C x 35 Sq.mm from 25KVA SL Transformer LV side to SL Feeder Pillar # 6 | RM | 20 |  | 0
3.12 | Terminate the cble on both ends c/w Cable Glands, Lugs etc. | Set | 2 |  | 0
3.13 | 5C x 25 Sq.mm Cable, all as per drgs between each SL Pole & Feeder Pillar & SL Pole. | RM | 950 |  | 0
3.14 | 5C x 16 Sq.mm Cable, all as per drgs between each SL Pole & Feeder Pillar & SL Pole. | RM | 3453 |  | 0
3.15 | 5C x 10 Sq.mm Cable, all as per drgs between each SL Pole & Feeder Pillar & SL Pole. | RM | 6260 |  | 0
3.16 | Street Lighting Cable Terminations on each Pole | Set | 289 |  | 0
3.17 | Street Lighting Cable Terminations on each Feeder Pillar | Set | 6 |  | 0
4 | Installation of Street Lighting Feeder Pillars :
Ref : Drg No # ARISE IIP/PICP/PN/TD/EL/SL-01/05
4.1 | Construct Feeder Pillar Foundations Approx 1000mm L X 650mm Wide X 600mm Deep, complete with access/entry & exit of cables, with suitable depth including cost for excavation, compaction and PCC laying.) Grade of RCC shall be C25 and PCC shall be C15. Fe 500 Reinforcement etc., | set | 6 |  | 0
4.2 | Install SL Feeder Pillars both Type -1 & Type - 2 | set | 6 |  | 0
5 | Earthing System :
Ref : Drg No # ARISE IIP/PICP/PN/TD/EL/SL-01/05
Ref : Drg No # ARISE IIP/PICP/PN/TD/EL/SL-04
| Earthing of Each feeder Pillar, Every 7th Street Lighting Pole, complete with 12.5mm - 1200mm Long Cu Earth Rod, CClamps, with 29Sqmm Bare Copper Conductor. | set | 49 |  | 0
| GRAND TOTAL- STREET LIGHT INSTALLATION WORKS |  |  |  | 0