## Sheet1
Republic of Congo (ROC)
Construciton & Comissioning of Borewell at PICP, Pointe Noire, ROC
S N | Description | Unit | Qtty | Unit Rate | Amount
1 | INVESTIGATION & MOBILIZATION
a. | Hydro-Geophysical Investigation of the site to Select and ascertain suitable drilling location to strike productive aquifer using appropriate technology | Job | 1
b. | Well Drilling Program by Vender (Time Schedules in discussion with Client) | Job | 1
c. | Mobilization of all necessary equipment, machinery personnel and demobilization of same upon completion. | Job | 1
2 | BOREHOLE DRILLING
a. | Allow for Fully preparation of motorized drilling rig equipment, preparation of mud pits, channel etc. | Job | 1
b. | Drilling of appropriate diameter borehole (375 mm to 450 mm) through Sedimentary formation for the installation of borehole casings down to the depth of:
i | Ground ground to 40 m | Mtr | 40
ii | from40 m to 100 m | Mtr | 60
3 | BOREHOLE CONSTRUCTION & DEVELOPMENT
a. | Supply 315mm dia Casing pipe ( PVC PN 16 SDR 13.6) | Mtr | 30
b. | Supply 200 mm dia.(SDR 13.6 PN16) PVC casings with esay fit joints . | Mtr | 70
c. | Supply of 200 mm dia. PVC (PN16, SDR 13.6) Production Casing/Screen pipe with slot size 2.5 mm to 6 mm properly | Mtr | 20
d. | Supply of (200 mm ) Bottom Bunk/Sump | Mtr | 3
e. | Installation of the assemblage of casings, screens and sump | Mtr | 100
f. | Supply and installation of washed gravel of appropriate grain size around Screen | Lum Sum | 1
g. | Sealing, cementation and grouting of the annulus down to the top of the gravel pack | Nos | 4
h. | Development of borehole until water becomes ( al least 48 to 72 hours Pumping ) clean with 20 Bar Cmpressor | Job | 1
i. | Geophysical Downhole Logging (NGR, Short Normal, Long Normal, R8, R32, SP, SPR) prior to Casing Run. | Job | 1
j. | Carry-out Aquifer Pumping Test to determine borehole yield and parameters. ( al least 72 hours) | Job | 1
k. | Physico-Chemical analysis of the raw water obtained from the borehole from Reconised Laboratory / Local govt approed as per Direction Client Engineer | Nos | 1
l. | Final Well Report (FWR) encompassing Well history; Geology, Geophysics, Drilling & Completions Records. | Job | 1
4 | PUMP INSTALLATION & WELL-HEAD CONSTRUCTION
a. | Supply Grundfos/ Fracklin submersible pump or equivalent complete with controller, cablings, switch- gear, safety switches, pilot tap etc (37 KW approx for Discharge 60-70 cum our suction head 40-50 m , Residual Free head 25 m ) | Nos | 1
b. | Add /Deduct for Pump Capacity Item 4 a | KW | R/o
c. | Supply of 4 G/16 Flexible cable | Mtr | 60
d. | Supply of (75 mm diameter high density HDPE Flexible riser pipes PN 16 SDR 13.6 . Rate includes all necessary fittings, Box Joining, Clamps , adoptors, Coupiling | Mtr | 60
e. | Installation of the assemblage of submersible pump and riser pipes flanges inside the drilled borehole. | Nos | 6
f. | Construction of the borehole head works rate includes all necessary pipe fittings, bend | Nos | 1
g. | Union connectors, Non return valve, Sampling point/Pilot Tap/16mm safety marine rope. | Lum Sum | 1
h. | Provisions of stainless-steel bolts and Nuts | Nos | 12
i. | Provide and install borehole cover, cage over the borehole head-works. Rate includes for concrete base surround to borehole and 65 mm dia flow meter (Ultrasonic / Electromagneticflow meter ) flow Range Range 0-100 cum/hour | Nos | 1