## BOQ
PN SEZ - ROC
MGK # 2 - 30KV MODIFICATION WORKS
SUPPLY & INSTALLATION OF EQUIPMENT / BOQ
S.NO | ITEM DESCRIPTION |  | UOM | QTY | Unit Rate | Amount | REMARKS
Work at station CT4
A | Supply Works
1 | Supply of 30 kV CB cubicles of Schneider Make, Model F400, equipped with MICOM Protection Relay, c/w with following Specifications : |  | Nos | 3 |  | 0
| Make | : Schneider Electric
| Model | : F400
| IAC | : AFLR
| Ur | : 36KV
| Un | : 30KV
| Ud | : 70KV 1 min
| Up | : 170KV 1 min
| Ir | : 1250A
| Ik | : 25kA / 3s
| Ip | : 63/65kA
| Ike | : 25kA / 3s
| Ipe | : 63/65kA
| Fr | : 50/60Hz
2 | Supply of Cable HNS 33 kV 1C X 300 MM² Alu XLPE. Armoured U/G Cable from CT#4 Sub-Station to 30KV T/Line Pole # 1. |  | RM | 6800 |  | 0
3 | Supply of Cable HNS 33 kV 1C X 300 MM² Alu XLPE. Armoured U/G Cable from Pole to Pole, across / under the existing 220KV HT Line. |  | RM | 1200 |  | 0
4 | Supply of 30KV Outdoor Termination Kits for 30 kV - 1C X 300 Sqmm XLPE Al Armoured Cables. |  | Nos | 36 |  | 0
5 | Supply of 30KV Indoor Termination Kits for 1C X 30 kV - 300 Sqmm XLPE Al Armoured Cables. |  | Nos | 12 |  | 0
6 | Supply of 30KV Cable Straight Through Jointing Kits for underground applications for 30 KV - 1C X 300 Sqmm XLPE Al. Armoured Cables. |  | Nos | 27 |  | 0
7 | Supply of concrete MV Cable markers with Arrow mark, for above ground Installations @ 100/200 mtrs ave. distance. |  | Nos | 12 |  | 0
| Total Amount for Supply Works |  |  |  |  | 0
B | Installation Works
1 | Installation of 30 kV CB cubicles collected from PN SEZ Stores. Schneider Make, Model F400 cubicles. |  | Nos | 3 |  | 0
2 | Installation of Cable HNS 33 kV 1C X 300 MM² Alu XLPE Armoured U/G Cable of 6 Runs from CT#4 Sub-Station to 30KV T/Line Pole # 1, including collecting the cable from PN SEZ Stores and transport to site locations.. |  | RM | 900 |  | 0
Scope shall include ….
- Excavation of cable trench approx 900 Mtrs X 1M wide X 1.6 M deep & Back Filling / Levelling and restoring site to normal, all as per local standards.
- Supply & Laying of Sand Bedding of 100mm + 100mm thk for cable protection.
- Supply of Danger Warning mesh (Red) as per local standards.
- Installation of Cable Markers collected from PN SEZ Stores.
- Supply & Installation of Cable Protection Covers along Poles Height and clamping and securing the cables & terminations..
3 | Supply of Cable HNS 33 kV 1C X 6 Runs X 300 MM² Alu XLPE. Armoured U/G Cable from Pole to Pole, across / under the HT Line, including collecting from PN SEZ Stores and transport to site locations.. |  | RM | 200 |  | 0
Scope shall include ….
- Excavation of cable trench approx 200 Mtrs X 1M wide X 1.6 M deep & Back Filling / Levelling and restoring site to normal, all as per local standards.
- Supply & Laying of Sand Bedding of 100mm + 100mm thk for cable protection.
- Supply of Danger Warning mesh (Red) as per local standards.
- Installation of Cable Markers collected from PN SEZ Stores.
- Supply & Installation of Cable Protection Covers on Poles incl clamping and securing the cables & terminations..
4 | Installation of 30KV Outdoor Termination Kits for 30 kV - 1C X 300 Sqmm XLPE Al Armoured Cables, incl collecting from PN SEZ Stores . |  | Nos | 36 |  | 0
5 | Installation of 30KV Indoor Termination Kits for 30 kV - 1C X 300 Sqmm XLPE Al Armoured Cables, incl collecting from PN SEZ Stores . |  | Nos | 12 |  | 0
6 | Installation of 30KV Cable Straight Through Jointing Kits for underground applications for 30 KV - 300 Sqmm XLPE Al Armoured Cables, incl collecting from PN SEZ Stores |  | Nos | 27 |  | 0
7 | Construc Cable Chambers of 1.4M X 1.4M X 1.6M deep with RCC and Heavy Duty Covers with locking mechanism, for 30KV U/G Cables Inspection. |  | Nos | 8 |  | 0
8 | Testing & Commissioning of Installed Cables & Panels |  | LS | 1 |  | 0
| Total Amount for Installation works |  |  |  |  | 0
| Grand Total Amount (Supply + Installation) |  |  |  |  | 0

## Installation. (hidden)
PN SEZ - ROC
MGK # 2 - 30KV MODIFICATION WORKS
INSTALLATION OF EQUIPMENT / BOQ
S.NO | ITEM DESCRIPTION | UOM | QTY | REMARKS
Installation Works at station CT4
1 | Installation of 30 kV CB cubicles collected from PN SEZ Stores. Schneider Make, Model F400 cubicles. | Nos | 3
2 | Installation of Cable HNS 33 kV 1C X 300 MM² Alu XLPE Armoured U/G Cable of 6 Runs from CT#4 Sub-Station to 30KV T/Line Pole # 1, including collecting the cable from PN SEZ Stores and transport to site locations.. | RM | 900
Scope shall include ….
- Excavation of cable trench approx 900 Mtrs X 1M wide X 1.6 M deep & Back Filling / Levelling and restoring site to normal, all as per local standards.
- Supply & Laying of Sand Bedding of 100mm + 100mm thk for cable protection.
- Supply of Danger Warning mesh (Red) as per local standards.
- Installation of Cable Markers collected from PN SEZ Stores.
- Supply & Installation of Cable Protection Covers along Poles Height and clamping and securing the cables & terminations..
3 | Supply of Cable HNS 33 kV 1C X 6 Runs X 300 MM² Alu XLPE. Armoured U/G Cable from Pole to Pole, across / under the HT Line, including collecting from PN SEZ Stores and transport to site locations.. | RM | 200
Scope shall include ….
- Excavation of cable trench approx 200 Mtrs X 1M wide X 1.6 M deep & Back Filling / Levelling and restoring site to normal, all as per local standards.
- Supply & Laying of Sand Bedding of 100mm + 100mm thk for cable protection.
- Supply of Danger Warning mesh (Red) as per local standards.
- Installation of Cable Markers collected from PN SEZ Stores.
- Supply & Installation of Cable Protection Covers on Poles incl clamping and securing the cables & terminations..
4 | Installation of 30KV Outdoor Termination Kits for 30 kV - 1C X 300 Sqmm XLPE Al Armoured Cables, incl collecting from PN SEZ Stores . | Nos | 36
5 | Installation of 30KV Indoor Termination Kits for 30 kV - 1C X 300 Sqmm XLPE Al Armoured Cables, incl collecting from PN SEZ Stores . | Nos | 12
6 | Installation of 30KV Cable Straight Through Jointing Kits for underground applications for 30 KV - 300 Sqmm XLPE Al Armoured Cables, incl collecting from PN SEZ Stores | Nos | 27
7 | Construc Cable Chambers of 1.4M X 1.4M X 1.6M deep with RCC and Heavy Duty Covers with locking mechanism, for 30KV U/G Cables Inspection. | Nos | 8
8 | Testing & Commissioning of Installed Cables & Panels | LS | 1